## Manufacturers sheet
PV module evaluation for rooftop PV systems in the Sultanate of Oman |  |  |  | Version 02 / 03 June 2019
No. | Item | Requirement | Actual value/ appearance | Your Response
Company name / Contact:
1 | Module type and Manufacturer
1.1 | What type(s) of module will be delivered ? | Clear type definition is required | Provide the type designation
| Is a special type for desert climate available? | Special type for desert climate are preferred
1.2 | Would you like to point out special features / new developments / improvements to us? | For example, special glass for less soiling, special backsheet materials…
1.3 | Does the module manufacturer or service provider have a subsidary, office or representative in Oman or at least in the Middle East? | Contact person and/or office in Oman/Middle East area | Provide contact
1.4* | Can the module manufacturer indicate reference projects with the offered module type(s) at point 1.1. or at least similar own products? | Experience with the offered module type in similar environment and / or installation types in Middle East or in other hot climate areas is required. In the best case track records are available. | Name reference projects (Minimum data: Country, Nominal Power, commissioning data, Module type(s))
2 | PV module electrical characteristics
2.1 | What are the available performance class width (Nominal power class)? | Desired power range per module in W is to be defined, e.g. 5 W steps. | Provide data sheet
2.2 | Please name the used sorting tolerance. | Are a positive sorting or standard sorting used?
2.3 | Is the maximum system voltage adequate? | Minimum 1000 V are necessary
2.4 | What is the maximum module efficiency?
2.5** | Has an Energy yield rating especially for hot climates been declared? | E.g. Energy Yield Label for desert climate by TUV Rheinland (New label documents test results for the evaluation of the real energy yield under desert conditions, Source see below table) | Provide label copy
2.4 | What is the efficiency loss at low irradiance? | Low irradiance (200W/m²) measurements are available and the efficiency loss compared to STC is to declare. Alternatively give the curves for different irradiance levels.
2.5 | What is the value for NMOT (NOCT)? | The operating module or cell temperature under the defined conditons (Irradiance: 800 W/m² / ambient temperature: 20°C, AM=1.5 and wind Speed: 1m/s) has to be specified. | Provide some proof
2.6 | How much does the module performance drop at high ambient temperatures? | Please provide the temperature coeffizient (Pmpp in %/K, maximum -0.40 %/K are expected).
3 | Modules Material and construction
3.1 | What cell type(s) is offered (point 1.1)? | Polycrystalline, Monocrystalline, Full or half cut cells, Thin film … (informative question)
3.2 | What Module size is offered? | 72 cells or 60 cells (not relevant for Thin Film) (informative question)
3.3 | Please indicate the module weight. | Please do it for every module size.
3.4 | Which module composition is offered? | Glass-Backsheet, Glass-Glass, bifacial module… Special backsheet material suitable for higher temperatures?
3.5 | What busbar technology is used (point 1.1)? | Please name the no. of used busbars.
3.6 | Will the serial number permanently be recognisable? | Serial no. is laminated in module etc.
3.7 | What kind of mechanical installation are recommended? | Mounting holes or wide range of clamping for installation etc.
3.8 | Is the type label reliable and readable?
3.9 | Is a special type of junction box suitable for higher temperatures involved? | Please indicate the type designation and if it is a standard or special type.
3.1 | Is the junction box component certification available? | Certification IEC 62790 | Provide a copy
3.11 | Which type of connector is involved? | Please provide the precise type definition!
3.12 | Is the connector component certification available? | Certification IEC 62852 | Provide a copy
3.13 | Which type of cable is selected?
3.14 | Is a cable component certification available? | Certification EN50618 | Provide a copy
3.15 | Is a Bill of material (BOM/ CDF) available and documentable? | Please specify, if the document will be made available after signing the contract and NDA?
4 | Certificates and warranties
4.1* | Is a valid IEC 61215 certification available? | Please provide the IEC 61215 certification. Is the new standard certified - 2016 series? (IEC 61215:2016 or IEC 61215:2005) | Provide a copy
4.2* | Is a valid IEC 61730 certification available? | Please provide the IEC 61730 certification. Is the new standard certified - 2016 series? (IEC 61730:2016 or IEC 61730:2004) | Provide a copy
4.3 | Was a positve sand abrasion testing performed with the module type? | Please specify if the sand abrasion testing was doing on glass and backsheet? (IEC 60068-2-68 or MIL 810 (Method 510.5) or others) | Provide a copy
4.4 | Has the resistance to saline athmosphere been proven? | Please specify a performed Salt mist corrosion test and provide the certificate (IEC 61701 certificate or other) | Provide a copy
4.5 | Wer the certificates issued by a generally recognized and accredited certification body? | Please state the certification body/bodies for the above and applicable further certificates.
4.6 | Were the tests performed by a test laboratory of the certification body or by a different subcontracted laboratory?
4.7 | Is a periodic factory inspection a part of the certification process? | Please state if all relevant production facilities are under periodic review by an independent inspector
4.8 | How long is the warranty period? | A manufacturer warranty period of minimum 10 years is expected.
4.9 | Which performance guarantee conditions apply? | A linear performance garantee of 25 years with a minimum nominal power of 80% are expected.
4.1 | Which performance restrictions and exclusions do apply? | - Are coastal site areas excluded? What does this mean for the required minimum distance to sea? | Provide warranty conditions
- Is the replacement of modules associated with extra costs (transport costs)?
- Are faulty modules possibly replaced by used or repaired components?
- Other relevant restrictions
5 | Advanced Testing
5.1 | Was an exteded damp heat test performed with the module type? | Please give the number of hours for the extended damp heat test and provide the document. (1000 h or more) | Provide some proof
5.2 | Was an extended thermal cycling test performed with the module type? | Please give the number of hours for the extended thermal cycling test and provide the document. (200 cycles or more) | Provide some proof
5.3 | Was an exteded UV performed with the module type? | Was the test performed with UV-AB irradiation according acc. IEC 61730-2? Please specify the energy quantity in kWh/m² (60 kWh/m² or more) | Provide some proof
5.4 | Were there any failed results in one or more of the advanced testing?
6 | Documentation
6.1 | Are all relevant data displayed on the datasheet? | Is a valid datasheet available and according to IEC 61730-1? | Provide a copy
6.2 | Are all required values acc. EN 50380 displayed on name plate? | Type label in acc. to EN 50380:2017 | Provide a copy
6.3* | Does the manual contain the normatively required information? | Is a manual available according to IEC 61730-1? | Provide a copy
- Are the methods of electrical and mechanical installation including necessary equipment discribed?
- Are necessary maintenance tasks defined?
6.4 | Are specific instructions given on the cleaning procedure?
7 | Quality and Environment Management in the module production
7.1 | Has the manufacturer a certified QM according to ISO 9001? |  | Provide a copy
7.2 | Has the manufacturer a standardized QM system for every production facilities or are multiple valid procedures and QM systems?
7.3 | Has the company a certified environmental management system established? | Is a valid certificate ISO 14001 available? | Provide a copy
7.4 | Has the company an occupational health and safety management system established? | Is a valid certificate for occupational health and safety management available, e.g. OHSAS 18001:2017 or ISO 45001:2018 | Provide a copy
7.5 | Final check: Are a 100% inline output power measurement system with the final assembled modules established?
7.6 | Final check: Are 100% inline electrical insulation measurements performed with the final assembled module?
7.7 | Final check: Are 100% inline electroluminescence imaging performed with the final assembled module for cristalline modules or similar quality measurements for thin film modules? | Which general assessment criteria are availabe (Cracks, soldering defects e.g.?)
Ranking
* | This is an obligatory requirement (Non-compliance is an exclusion criterion)
** | https://www.researchgate.net/publication/311439722_ENERGY_RATING_LABEL_FOR_PV_MODULES_FOR_IMPROVING_ENERGY_YIELD_PREDICTION_IN_DIFFERENT_CLIMATES

## Documentation IEC 61730 (hidden)
IEC 61730-1 | Edition 2.0 2016-08
Photovoltaic (PV) module safety qualification –
Part 1: Requirements for construction
5.2.3 Documentation
PV modules shall be supplied with documentation describing the methods of electrical and
mechanical installation as well as the electrical ratings of the PV module. The documentation
shall state the Class under which the PV module was qualified and any specific limitations
required for that Class. The documentation shall state the environmental conditions to which
the module has been qualified, which by default includes a temperature range of –40 °C to
+40 °C and wind/snow load including safety factor. It shall be ensured that appropriate
documentation for safe installation, use, and maintenance is available to installers and
operators.
For identical PV modules it is considered to be sufficient that one set of documentation is
supplied with the PV module shipping unit.
Environmental conditions to which a PV module has been qualified may include IEC 61701 or
IEC 62716.
The documentation shall contain the following information:
• all information required by 5.2.2.1 with exception of c), d) and e);
• recommended maximum series/parallel PV module configurations;
• the current rating of overcurrent protection, as determined in MST 26. Guidance to
determine current rating may be given in to IEC 60269-6
• manufacturer’s stated tolerance for Voc, Isc and maximum power output Pmax under
standard test conditions;
• temperature coefficient for voltage at open-circuit;
• temperature coefficient for maximum power; and
• temperature coefficient for short-circuit current.
All electrical data shall be shown as relative to standard test conditions (1 000 W/m2,
(25 ± 2) °C, AM 1,5 according to IEC 60904-3).
The electrical documentation shall include a detailed description of the electrical installation
wiring method to be used. This description shall include:
• the minimum cable diameters for PV modules intended for field wiring;
• any limitations on wiring methods and wire management that apply to the junction box for
the PV module;
• the size, type, material, and temperature rating of the conductors to be used;
• type of terminals for field wiring;
• specific PV connector model/types and manufacturer to which the PV module connectors
can be mated;
• the bonding method(s) to be used (if applicable) shall be specified. All provided or
specified hardware shall be identified in the documentation;
• the type and ratings of bypass diode to be used (if applicable);
• limitations to the mounting situation (e.g. slope, mounting means, cooling);
• a statement indicating the fire rating(s) and the applied standard, or a statement that
resistance to external fire sources was not evaluated, as well as the limitations to that
rating (e.g. installation slope, sub structure or other applicable installation information);
• a statement indicating the minimum mechanical means for securing the PV module (as
evaluated during the mechanical load test (MST 34)); and
• a statement indicating the maximum altitude the PV module is designed for. De-ratings
can be applied.
The documentation for roof mounting shall include:
• a statement indicating the minimum mechanical means for securing the PV module to the
roof (as evaluated during the mechanical load test according (MST 34);
• details of the specific parameter(s) when the fire rating is dependent on a specific
mounting structure, specific spacing, or specific means of attachment to the roof or
structure.
The documentation shall include a statement advising that external or otherwise artificially
concentrated sunlight shall not be directed onto the front or back face of the PV module (if not
qualified for).
Assembly instructions shall be provided with a product shipped in subassemblies, and shall
be detailed and adequate to the degree required to facilitate complete and safe assembly of
the product to specifications set forth in the IEC 61730 standard series.
To facilitate proper system sizing the manufacturer shall include relevant parameters in the
installation instructions that allow system layout based not only on STC values given in the
documentation. For example a safety factor for Voc and Isc of 1,25 is recommended since
irradiance is often higher then 1 000 W/m2 and temperature below Licensed to TÜV Media GmbH / TÜV Rheinland Group 25 °C may raise Voc.

## Nameplates (hidden)
EN 50380:2017 (E)
Ok? | 5.0 Marking information
…
5.2 Mandatory information
Y
Y | 5.2.2 Module identification
No | a) Name, registered trade name or registered trade mark of manufacturer;
Y | b) type or model number designation;
Y? | c) serial number;
d) date and place of manufacture; alternatively serial number allowing to trace the date and place of manufacture;
5.2.3 Electrical information
The following electrical data shall be shown as relative to standard test conditions (1 000 W/m2, 25 °C, AM 1,5G according to CLC/TS 61836).
Manufacturer’s stated tolerance shall be given under standard test conditions (STC):
a) Polarity of terminals or leads;
b) PV connectors shall be clearly marked indicating the terminal polarity.
c) PV connectors shall be marked with a symbol “Do not disconnect under load“, as given in EN 61730-1:2016, Annex A (e.g. graphical symbol IEC 60417-6070). Symbol or warning notice shall be imprinted or marked close to connector.
d) Maximum overcurrent protection rating (see 4.3.2 c));
e) “Maximum system voltage” or Vsys;
f) Class of protection against electrical shock, in accordance to EN 61730-1.
For Class II and Class 0 PV modules, the graphical symbol IEC 60417-6042: Caution, risk of electric shock , shall be applied near the PV module electrical connection means.
PV modules provided with a functional earth connection shall be marked with the graphical symbol IEC 60417-5018: Functional earthing .
PV modules provided with terminals for field wiring rated only for use with copper wire shall be marked, at or adjacent to the terminals, with the statement “Use copper wire only”, “Cu only”, or the equivalent.
PV modules provided with terminals for field wiring rated only for use with a different specific wiring material shall be marked with a similar statement referring to the rated material.
g) “Voltage at open-circuit” or “Voc” including rated production tolerances;
h) “Voltages at maximum power point” or “VPmax” including rated production tolerances;
i) “Current at maximum power point”; or “IPmax” including rated production tolerances;
j) “PV module maximum power” or “Pmax” including rated production tolerances;
k) “Current at short-circuit”; or “Isc” including rated production tolerances.

## Data sheet (hidden)
DIN EN 50380 VDE 0126-380:2018-07
Da­ten­blatt- und Ty­pen­schild­an­ga­ben von Pho­to­vol­ta­ik-Mo­du­len;
Deutsche Fassung EN 50380:2017
Art/Status: Norm, gültig
Ausgabedatum: 2018-07
VDE-Artnr.: 0100471
4.3 Mandatory information
4.3.1 General
This subclause lists the mandatory information to be provided for PV modules according to this standard.
4.3.2 Electrical, including wiring, information
The documentation shall contain the following electrical information:
a) polarity of terminals or leads;
b) “Maximum system voltage” or Vsys;
c) Maximum overcurrent protection (OCP) rating
Overcurrent protection devices with a 1hr, 1,35 IR overload rating, where IR is the rated value of the overcurrent protection device, are recommended.
NOTE Compliance can be checked according to EN 61730–2 MST 26. IR -rating can be determined using procedure in Annex A.
d) Class of protection against electrical shock, in accordance with EN 61730-1 (see further details in 5.2.3 f))
The following electrical data shall be shown as relative to standard test conditions (1 000 W/m2, 25 °C, AM 1,5G according to CLC/TS 61836) and after stabilization.
Manufacturer’s stated rated production tolerance shall be given also under standard test conditions
e) “Voltage at open-circuit” or “Voc” including rated production tolerance
f) “Voltages at maximum power point” or “VPmax” including rated production tolerance
g) “Current at maximum power point”; or “IPmax” including rated production tolerance
h) “PV module maximum power” or “Pmax ” including rated production tolerance
i) “Current at short-circuit”; or “Isc” including rated production tolerance
Electrical values after stabilization according to the IEC 61215 series shall be verifiable and within the specified rated production tolerances and uncertainties. A procedure is given in Annex B
NOTE 1 Example: Pmax = 250,0 W, rated production tolerance 3 %, binning + 5 W / - 0 W.
That means that modules from 250,0 W to 254,9 W are sorted in one bin, rated Pmax = 250,0 W. Tolerance of 3 % results on deviations from 250,0 W from 242,5 W to 257,5 W.
j) Relative temperature coefficients in [%/K] for Isc, Pmax and Voc at STC
NOTE 2 The values for IMPP and VMPP can be provided
k) State if temperature coefficients are linear.
In cases of nonlinear temperature coefficients according to EN 60904-10 further information regarding temperature coefficients shall be provided.
l) The minimum cable diameters for PV modules intended for field wiring
m) Any limitations on wiring methods and wire management that apply to the junction box for the PV module
n) The size, type, material, and temperature rating of the conductors to be used
o) Type of terminals for field wiring
p) Specific PV connector model/types and manufacturer to which the PV module connectors can be mated
q) The bonding method(s) to be used (if applicable) shall be specified. All provided or specified hardware shall be identified in the documentation;
r) A statement if protective devices (e.g. bypass diode etc.) are part of the PV module. A statement if the protective device is replaceable.
4.3.3 Mechanical information
a) A statement indicating the design load for each mounting method (clamps, bolts, etc.) for securing the module.
b) Limitations for each mounting method (slope, mounting means, air gap between structure and module, rack mounting, roof or building integrated / attached, etc.).
c) Limitations for each mounting method if fire rating is dependent on mounting method.